Power System Operation and Control (EE-421)

Sr. No.					Lab Experiment

- Operating a switching station with two busbars and different voltages.

- To study operation of double busbar system with load.

- To perform the different operation of busbar coupling.

- 3 Phase Power Generation and  Synchronization of Supply with Wapda

- Operation of Single-phase current transformer

- To study the Single-phase CT at over-current

- Operation of Three-phase current transformer

- Operation of Three-transformer summing circuit

- To study the Single-phase voltage transformer

- To study Three single-pole voltage transformers

- Two single-pole voltage transformers

- Series connection of two lines

- Operation of Parallel connection of two lines

- Investigating the performance with isolated neutral point connection in the case of a fault to earth

- Observing the usage of Petersen Suppression Coil

- Investigating the effect of parallel compensation on the voltage stability

Experiment No. # 01

DOUBLE BUSBAR BASIC SYSTEM

Objectives:

- Operating a switching station with two busbars and different voltages.

Equipments:

- 1 IT 6017 Three-phase power supply

- 2 IT 6019 Power circuit breaker

- 1 IT 6021 Double busbar with 4 disconnectors

- 1 IT 6003 Three-phase transformer

- 1 IT 6002 Overhead line model

- 2 IT 6035 Moving-iron ammeter (2.5 A)

- 2 IT 6037 Moving-iron voltmeter (600 V)

Single-pole diagram

EXPERIMENT N°1: DOUBLE BUSBAR BASIC SYSTEM

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Special care must be taken to ensure that the individual phases are connected correctly in order to avoid later short-circuits.

In order to fully utilise the possibilities of the double busbar system, the busbars should be supplied from two different voltages: the voltage at the beginning of the overhead line model (busbar 1) and the voltage at the end of the line model (busbar 2).

Set primary-side of the three-phase transformer in delta connection 380V and set the secondary-side to star UN-15%.

Insert all plugs connecting the capacitances to the line model.

Initially switch on the main switch in order to supply the three-phase transformer and the line model.

The switching sequence of the two power circuit breakers (K1, K2) and of the two

disconnectors (Q1,Q2), in order to connect the busbars, is:

1. Initially activate the disconnector

2. Then activate the power circuit breaker.

E.g. Busbar 1: Disconnector Q1 on - Power circuit breaker K1 on.

Measure the busbar voltages:

U1 = .......... (V) 		U2 = .................... (V)

Which of the two busbars has the higher voltage?

..................................................................................................................Why?

(Hint: Refer to §1.4.1, manual DL GTU 102.2)

....................................................................................................................................

The switching sequence in order to disconnect the busbars is:

1. Initially switch off the power circuit breaker

2. Then switch off the disconnector.

E.g. Busbar 2: power circuit breaker K2 off - Disconnector Q2 off.

NOTE

The disconnectors are interlocked with the related power circuit breakers and faulty switching sequence is not allowed: in this case a warning signal is produced.

EXPERIMENT NO. 02

DOUBLE BUSBAR SYSTEM WITH LOAD

Objectives:

- Busbar transfer with interruption of the power supply to the consumer.

- Switching sequence for disconnectors and power circuit breakers.

Equipments

- 1 IT 6017 Three-phase power supply

- 3 IT 6019 Power circuit breaker

- 1 IT 6021 Double busbar with 4 disconnectors

- 1 IT 6004 Resistive load

- 1 IT 6003 Three-phase transformer

- 1 IT 6002 Overhead line model

- 3 IT 6035 Moving-iron ammeter (2.5 A)

- 2 IT 6037 Moving-iron voltmeter (600 V)

Single-pole diagram

EXPERIMENT N°2: DOUBLE BUSBAR SYSTEM WITH LOAD

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Special care must be taken to ensure that the individual phases are connected correctly in order to avoid later short-circuits.

In order to fully utilise the possibilities of the double busbar system, the busbars should be supplied from two different voltages: the voltage at the beginning of the overhead line model (busbar 1) and the voltage at the end of the line model (busbar 2).

Set primary-side of the three-phase transformer in delta connection 380V and set the secondary-side to star UN-15%.

Insert all plugs connecting the capacitances to the line model.

Connect the three-phase balanced ohmic load to outgoing power circuit breaker and set the load resistance value to R5: the load must be supplied alternatively from busbar 1 or from busbar 2 as desired.

Initially switch on the main switch in order to supply the three-phase transformer and the line model.

First of all a connection is to be established between busbar 1 and the load.

Switching sequence:

1. Initially activate the disconnectors Q1 and Q3.

2. Then activate the power circuit breaker K1: the bus bar 1 is alive.

3. Now activate the power circuit breaker K3: the busbar 1 feeds the load.

4. Finally activate in sequence the disconnector Q2 and the power circuit breaker K2: the busbar 2 is alive also.

Measure the busbar voltages:

U1 = .......... (V) 		U2 = .................... (V)

Measure the circuit currents:

I1 = ............ (A) 		I2 = ...........(A) 		I = ...............(A)

It must result I1 = I and I2 = 0: busbar 1 feeds the load.

Now carry out a bus transfer so that the supply of the load is performed from busbar 2.

The switching sequence in order to transfer the load from the busbar 1 to busbar 2 is:

1. Initially switch off the power circuit breaker K3.

The load is isolated: this phenomenon normally do not occur in practice with regard to network operation.

2. Then switch off the disconnector Q3.

3. Now switch on the disconnector Q4.

4. Finally switch on again the power circuit breaker K3.

Measure the voltage at both bus bars:

U1 =............ (V) 		U2 =................. (V)

Measure the circuit currents:

I1 =............. (A) 	I2 =................. (A) 		I =.................. (A)

It must result I1 =0 and I2 = I: now busbar 2 feeds the load.

NOTES

- The incoming disconnectors are interlocked with the related power circuit breakers and faulty switching sequence is not allowed: in this case a warning signal is produced.

- The outgoing disconnectors are both interlocked with the outgoing power circuit breaker and faulty switching sequence is not allowed: in this case a warning signal is produced.

EXPERIMENT N0. 03

BUSBAR COUPLING

Objectives:

- Busbar coupling and busbar transfer without interruption of the power supply to the consumer.

- Switching sequence for disconnectors and power circuit breakers.

Equipments

- 1 IT 6017 Three-phase power supply

- 4 IT 6019 Power circuit breaker

- 1 IT 6020 Double busbar with 2 disconnectors

- 1 IT 6021 Double busbar with 4 disconnectors

- 1 IT 6004 Resistive load

- 1 IT 6003 Three-phase transformer

- 1 IT 6002 Overhead line model

- 3 IT 6035 Moving-iron ammeter (2.5 A)

- 2 IT 6037 Moving-iron voltmeter (600 V)

Single-pole diagram

EXPERIMENT N°3: BUSBAR COUPLING

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Special care must be taken to ensure that the individual phases are connected correctly in order to avoid later short-circuits.

In order to fully utilise the possibilities of the double busbar system, the busbars should be supplied from two different voltages: the voltage at the beginning of the overhead line model (busbar 1) and the voltage at the end of the line model (busbar 2).

Set primary-side of the three-phase transformer in delta connection 380 V and set the secondary-side to star UN-15%.

Insert all plugs connecting the capacitances to the line model.

Connect the three-phase balanced ohmic load to outgoing power circuit breaker and set the load resistance value to R5: the load must be supplied alternatively from busbar 1 or from busbar 2 as desired.

Initially switch on the main switch in order to supply the three-phase transformer and the line model.

First of all a connection is to be established between busbar 1 and the load.

Switching sequence:

1. Initially activate the disconnectors Q1 and Q3.

2. Then activate the power circuit breaker K1: the bus bar 1 is alive.

3. Now activate the power circuit breaker K3: the busbar 1 feeds the load.

4. Finally activate in sequence the disconnector Q2 and the power circuit breaker K2: the busbar 2 is alive also.

Measure the busbar voltages:

U1 = .......... (V) 	U2 = .................... (V)

Measure the circuit currents:

I1 = ............ (A) 	I2 = ...........(A) 	I = ...............(A)

It must result I1 = I and I2 = 0: busbar 1 feeds the load.

Now carry out a bus transfer so that the supply of the load is performed from busbar 2 without interrupting the supply to the load.

The switching sequence in order to transfer the load from the busbar 1 to busbar 2 without isolating the load is:

1. Initially switch on the coupling disconnectors Q11 and Q21.

2. Then switch on the coupling power circuit breaker K4: thus the two busbar have the same potential.

3. Now switch on the outgoing disconnector Q4.

4. Then switch off the outgoing disconnector Q3

5. Finally switch off again the coupling power circuit breaker K4 and then switch off the coupling disconnectors Q11 and Q21: thus the two busbars are again separated.

Measure the voltage at both busbars:

U1 = ............(V) 	U2 = ................. (V)

Measure the circuit currents:

I1 = .............(A) 	I2 = .................(A) 	I = ..................(A)

It must result I1 = 0 and I2 = I: now busbar 2 feeds the load.

EXPERIMENT NO.04

3 Phase Power Generation and synchronization of supply with wapda

Apparatus:

- Ammeter (IT 3035)

- Voltmeter (IT 6038)

- Wattmeter (IT 6048)

- Power factor Meter (IT 6049)

- 3 Phase Power Meter (IT 6041)

- Double Frequency Meter (IT 6041)

- Variable DC Power Supply Unit (IT 6000)

- Variable 3Phase Power Supply Unit (IT 6000)

- Digital MultiMeter (UTI-T55)/ Tachometer (DT 2234A)

- Three-Phase Synchronous Machine (DL 1026A)

- Shunt Dc Motor (DL 1023PS)

- Magnetic Powder Brake (DL 1019P)

- Phase Sequence Indicator (IT 6040)

- Synchronocsope (IT 6053)

- Power Circuit (IT 6019)

- Set of Experiment Cables

Theoretical Background:

As the world becomes more reliant on electric power to function and grow, backup power systems, such as generators, are playing an increasingly significant role in ensuring uninterrupted supply of power. Your choice of a generator depends primarily on the amount of backup power that is required for your specific application. Oftentimes, you may require just a minimum supply of backup power to ensure uninterrupted functioning of basic appliances or mission critical equipment.

Why are synchronous generators operated in parallel?

- Many generators can supply a bigger load than one machine by itself.

- Having many generators increases the reliability of the power system, since failure of any one of them does not cause a total power loss to the load.

- Having many generators operating in parallel allows one or more of them to be removed for shutdown and preventive maintenance.

- If only one generator is used and it is not operating at near full load, then it will be relatively inefficient. But with many machines it is possible to operate only a fraction of them. The ones that do operate near full load and therefore more efficiently.

Generators being paralleled with a running power system

What are the conditions for paralleling?

- The RMS line voltages of the two generators must be equal.

- The two generators must have the same phase sequence.

- The phase angles of the two a phases must be equal.

- The frequency of the new generators, called the oncoming generator, must be slightly higher than the frequency of the running system.

The three-light-bulb method for checking phase sequence.

Three-Phase Synchronous Machine (DL 1026A)

Machine with smooth inductor and three-phase stator armature winding for operation either as alternator or synchronous motor

- Alternator: 1.1 kVA

- Motor: 1 kW

- Voltage: 220/380 V Δ/Y

- Current: 2.9/1.7 A

- Speed: 3000 min-1

- Dc rotor excitation winding

Shunt Dc Motor (DL 1023PS)

- Power: 1.8 kW

- Voltage: 220 V

- Speed: 3000 min-1

- Excitation voltage: 170 V

Circuit Diagram:

Fig: Motor Generator Set for 3 phase Generation

Here AC generator is used as load on dc shunt motor. As we know generator has counter torque

which opposes input power given by dc shunt motor and counter torque is dependant load

current. Hence on increasing load on generator, it will develop more counter torque, thus more

load will be reflected on dc shunt motor.

N = (Speed Equation of DC Motors)

Ia= (Armature current equation)

If = (Field current equation)

In shunt dc motor field is connected in parallel with armature. From its speed equation it is vivid,

on increasing load speed will drop due to increased armature drop.

Decrease in speed will decrease back e.m.f. and consequently armature current will increase. As

for as field current is concern, it will remain constant until and unless terminal voltage remains

constant.

PROCEDURE:

- Make the circuit as shown in figure.

- Apply the Variable Voltage Supply

- Start the motor by pressing GREEN switch "ON" without load.

- Note down the readings of instrument connected.

- Check the V rms, frequency, Phase Sequence (R-Y-B) of 3 Phase generator for Synchronization using dark Lamps Method

- Now connect electrical load on generator and start increasing load in steps.

- After every step, note down readings of instrument connected.

- Draw curves between armature current and load current and between speed and load Current

OBSERVATIONS AND CALCULATION:

| Sr. No | V DC (V) Motor | I DC (I) Motor | Vrms (V) (Wapda) | F (Hz) | Rpm | Vrms g (V) | FG (Hz) | VDC Excitation | IDC Excitation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 |  |  |  |  |  |  |  |  |  |
| 02 |  |  |  |  |  |  |  |  |  |
| 03 |  |  |  |  |  |  |  |  |  |
| 04 |  |  |  |  |  |  |  |  |  |
| 05 |  |  |  |  |  |  |  |  |  |

EXPERIMENT N0. 05

SINGLE-PHASE CURRENT TRANSFORMER

Objectives:

- Determining the transformation ratio of a current transformer for various primary currents and investigating the influence of the load on the transformation ratio.

- To explain the terms ratio error (current error), accuracy class and rated accuracy limit factor.

Strumenti:

- 1 IT 6004 Resistive load

- 1 IT 6016 Experiment transformer

- 1 IT 6024 CT load

- 1 IT 6043 Single-phase current transformer

- 4 IT 6034 Moving-iron ammeter (1000 mA)

- 2 IT 6036 Moving-iron ammeter (5 A)

- 4 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

EXPERIMENT N°1: SINGLE-PHASE CURRENT TRANSFORMER KN =

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Do not forget the current transformer may not be operated in open circuit on its secondary side!

The resistive load is located in the primary circuit and for this experiment the three

individual resistors are connected in parallel: set the load resistance value to R3.

Set the resistive CT load on the secondary side to an initial value of 0%: this means that the only load in the secondary circuit is the ammeter in the circuit and its internal resistance is negligible.

Connect the current transformer so that the resulting current transformation ratio is 1:1. Set the supply voltage 0 ÷ 250 V and starting from 0 V, increase the value of the voltage to obtain the current values I1 = 0.1 A to 1 A in steps of 0.1 A in the primary circuit of the current transformer.

Read off the corresponding secondary currents I2 in the secondary circuit and enter these values in the following table.

Transformation ratio 1:1

| I1 (A) | 0,2 | 0,3 | 0,4 | 0,5 | 0,6 | 0,7 | 0,8 | 0,9 | 1,0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I2 (A) |  |  |  |  |  |  |  |  |  |
| Fi (%) |  |  |  |  |  |  |  |  |  |

Calculate the current error

and enter the results in the table: determine the maximum current error

Fimax = …………………..

The rated load of the current transformer is 5 A, i.e., 5Ω at a secondary rated current of 1 A.

Set the resistance load for the current transformer on the secondary side to approximately 5Ω, and repeat the above experiment.

Enter the measured and calculated value in the following table.

Transformation ratio 1:1

| I1 (A) | 0,2 | 0,3 | 0,4 | 0,5 | 0,6 | 0,7 | 0,8 | 0,9 | 1,0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I2 (A) |  |  |  |  |  |  |  |  |  |
| Fi (%) |  |  |  |  |  |  |  |  |  |

Maximum current error Fimax = ……………..

To represent better the influence of the load on the secondary current record the voltage on the secondary side as function of the resistance load of the current transformer at a constant primary current.

To do this, connecting the voltmeter to the terminals 2.1 and 2.2 of the current transformer, vary the resistance load of the current transformer from 0Ω to the maximum.

For this experiment, the current in the primary circuit of the transformer must be set to 1 A and be held constant by regulating the supply voltage.

Enter the measured values in the following table.

Transformation ratio 1:1

| Carico (Ω) | 0 | 5 | 10 | 15 | 20 | 30 | 40 | 50 | 60 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| U2 (V) |  |  |  |  |  |  |  |  |  |

Note: If you want to test the performance of the current transformer with transformation ratio of 5:1, replace the 1 A ammeter on the primary side with another one with 5 A range and connect the current transformer so that the resulting current transformation ratio is 5:1.

Set the resistive load located on the primary circuit to the value R7 and repeat the

same procedure as before.

Transformation ratio 5:1

| I1 (A) | 0,1 | 1,5 | 2,0 | 2,5 | 3,0 | 3,5 | 4,0 | 4,5 | 5,0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I2 (A) |  |  |  |  |  |  |  |  |  |
| Fi (%) |  |  |  |  |  |  |  |  |  |

Maximum current error Fimax = ……………..

EXPERIMENT No. 06

SINGLE-PHASE CT AT OVERCURRENT

Objectives:

- Testing the performance of the current transformer at over current.

Equipments:

- 1 IT 6004 Resistive load

- 1 IT 6016 Experiment transformer

- 1 IT 6024 CT load

- 1 IT 6043 Single-phase current transformer

- 2 IT 6036 Moving-iron ammeter (5 A)

EXPERIMENT N°2: SINGLE-PHASE CT AT OVERCURRENT

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Do not forget that the current transformer may not be operated in open circuit on its secondary side!

The resistance load is located in the primary circuit and for this experiment the three individual resistors are connected in parallel: set the load resistance value to R7.

Set the resistive load for the current transformer on the secondary side to 0.5 Ω.

Connect the current transformer so that the resulting current transformation ratio is 1:1.

Set the supply voltage 0÷250 V and starting from 0 V, increase the value of the voltage to obtain the values I1 = 1 A to 5 A in steps of 0.5 A in the primary circuit of the current transformer.

Read off the corresponding currents b in the secondary circuit and enter these values in the following table.

Transformation ratio 1:1

| I1 (A) | 0,1 | 0,5 | 2,0 | 2,5 | 3,0 | 3,5 | 4,0 | 4,5 | 5,0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I2 (A) |  |  |  |  |  |  |  |  |  |
| Fi (%) |  |  |  |  |  |  |  |  |  |

Calculate the current error and enter the result in the table.

Neglecting the ammeter resistance on the secondary side, the current transformer load is 0.5Ω. At the rated load of 5 VA the secondary rated current is

At this value determine the primary current I1 and the current error: verify if the specified accuracy class is observed.

EXPERIMENT NO. 07

THREE-PHASE CURRENT TRANSFORMER

Objectives:

- Assembling the common current transformer circuit for measurement on three-phase network.

Equipments:

- 1 IT 6000 Three-phase power supply

- 1 IT 6004 Resistive load

- 1 IT 6044 Three-phase current transformer

- 4 IT 6034 Moving-iron ammeter (1000 mA)

EXPERIMENT N°3: THREE-PHASE CURRENT TRANSFORMER

Experiment procedure

Assemble the circuit according to the foregoing topographic diagram.

Do not forget that the current transformer may not be operated in open circuit on its secondary side!

The resistive load, located in the primary circuit, is star connected and set to resistance value R6 for every phase.

Connect the three-phase current transformer so that the resulting current transformation ratio is 1:1.

Starting from 0 V, increase the value of the supply voltage to obtain 1 A on the primary circuit.

Measure the three primary current alternately and read off the secondary currents with the neutral conductor N connected or disconnected.

N connected N disconnected

|  | N connected | N discounted |
| --- | --- | --- |
| IL1 (A) I1 (A) | 1 …………… | 1 …………… |
| IL2 (A) I2 (A) | 1 …………… | 1 …………… |
| IL3 (A) I3 (A) | 1 …………… | 1 …………… |

The three measured currents must be approximately equal in both cases; slight deviations may be explained by the components tolerances.

Asymmetrical loads can also be measured with this circuit.

Change only the resistive loads of the phases L2 and L3 to the value R5.

Increase the supply voltage to obtain a primary current ILI = 1 A.

Measure the three secondary currents, once with and once without the neutral conductor N connected.

|  | N connected | N discounted |
| --- | --- | --- |
| I1 (A) | ………… (1) | …………(0,9) |
| I2 (A) | …………(0,7) | …………(0,75) |
| I3 (A) | …………(0,7) | …………(0,75) |

Now, when the circuit is not alive, disconnect the conductor L3 at the output side of the threephase power supply.

Repeat the above measurements.

|  | N connected | N discounted |
| --- | --- | --- |
| I1 (A) | ………… (1) | …………(0,68) |
| I2 (A) | …………(0,7) | …………(0,7) |
| I3 (A) | …………(0) | …………(0) |

Note: The values in brackets are for information only.

EXPERIMENT NO. 08

THREE – TRANSFORMER SUMMING CIRCUIT

Objectives:

- Measuring the zero-phase sequence current of a three-phase system. (For an explanation of the term "zero-phase sequence current" please refer to

Equipments:

- 1 IT 6000 Three-phase power supply

- 1 IT 6004 Resistive load

- 1 IT 6044 Three-phase current transformer

- 4 IT 6034 Moving-iron ammeter (1000 mA)

EXPERIMENT N°4: THREE – TRANSFORMER SUMMING CIRCUIT

Experiment procedure

Assemble the circuit according to the foregoing topographic diagram.

Do not forget that the current transformer may not be operated in open circuit on its secondary side!

The resistive load, located in the primary circuit, is star connected and set to resistance value R6 for every phase.

The three-phase current transformer is connected as summing circuit, with current

transformation ratio 1:1.

Starting from 0 V, increase the value of the supply voltage to obtain a current of about 0.8 A on the primary circuit.

Measure the zero-phase sequence current Io once with three-phase symmetric load and once with asymmetric load, by disconnecting the conductor L3 from the resistive load when the circuit is not alive.

| Load | IL1 (A) | Io (A) |
| --- | --- | --- |
| Symmetric | 0.8 | ……………. (0) |
| Asymmetric | 0.8 | …………..(0,8) |

Now disconnect the neutral conductor N at the output side of the three-phase power supply.

Repeat the measurements.

| Load | IL1 (A) | Io (A) |
| --- | --- | --- |
| Symmetric | 0.8 | ……………. (0) |
| Asymmetric | 0.7 | ……………. (0) |

Note: The values in brackets are for information only.

EXPERIMENT NO. 09

SINGLE-PHASE VOLTAGE TRANSFORMER

Objectives:

- Determining the transformation ratio of a voltage transformer for various primary voltages and investigating the influence of the load on the transformation ratio.

- To explain the terms ratio error (voltage error) and accuracy class

Equipments:

- 1 IT 6016 Experiment transformer

- 1 IT 6025 VT load

- 1 IT 6045 Single-phase voltage transformer

- 4 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

EXPERIMENT N°6: SINGLE-PHASE VOLTAGE TRANSFORMER

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Initially do not connect the VT load to the two secondary windings: this means that the only load in the secondary side is the high-ohm one of the voltmeter.

Do not forget that the voltage transformer must never be short-circuited on its secondary side!

Set the supply voltage 0 ÷ 250 V and starting from 0 V, increase the value of the supply voltage to obtain the values U1 = 25 V to 225 V in steps of 25 V in the primary circuit of the voltage transformer.

Read off the corresponding voltages U2 in the secondary and U3 in the tertiary circuit; enter these values in the following table.

| U1 (V) | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| U2 (V) FU2 (%) |  |  |  |  |  |  |  |  |  |
| U3 (V) FU3 (%) |  |  |  |  |  |  |  |  |  |

Calculate the voltage errors

and enter the results in the table.

Determine the maximum voltage errors:

FU2max = ……… %	 	FU3max = ……… %

Being S the apparent power drawn by the voltage transformer, the rated load at secondary and tertiary circuit is

To study the influence of the load on the transformation ratio, now connect the fixed basic load to tertiary and the variable load (330Ω min) to secondary, as illustrated in the topographic diagram.

Set the primary voltage to U1 = 220 V and record the voltages U2 on the secondary side as a function of the load.

Enter the measured values in the following table.

| Load (%) | 0 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- |
| U2 (V) |  |  |  |  |  |

Read off also the voltage U3 on the tertiary side:

U3 = ………. (V)

With the rated voltage applied to the primary side, calculate the apparent power drawn by the two secondary windings when the secondary variable load is set to the minimum value of 330Ω and the tertiary load is 220Ω:

S2 = ……… VA			 F3 = ……… VA

Compare the measured value with that specified in the transformer data.

EXPERIMENT No. 10

THREE SINGLE-PHASE VOLTAGE TRANSFORMERS

Objectives:

- Assembling the common voltage transformer circuit for measurements in three-phase network.

- Measuring the residual voltage in a three-phase system with a fault to ground.

Equipments:

- 1 IT 6000 Three-phase power supply

- 1 IT 6046 Three-phase voltage transformer

- 4 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram. Initially do not use the connection to simulate a fault to ground.

Do not forget that the voltage transformer must never be short-circuited on the secondary side!

The three-phase voltage transformer is connected as three single-pole isolated transformers:

the secondary side in star connection supplies an image of the three-phase voltages of the network while the auxiliary windings are connected in series and serves to measure the faults to ground.

Set the supply voltage to UL12 = 380 V and measure the voltages of secondary winding:

Uvw = ……… V 	Uwu = ……… V 	Uuv = ……… V

and the voltage between terminals "n" and "e" of the three individual auxiliary windings connected in series:

Uen = ……… V

In the symmetrical load operation, the residual voltage Uen = 0 V and the voltage transformer responds as expected according to the transformation ratio.

Now, in order to simulate a fault to ground in a network with isolated neutral point, remove the connection of the neutral conductor at the output side of the three-phase power supply and connect the phase L3 to star point N of the primary winding (see detailed diagram to simulate a fault to ground).

In this experiment, great care must be taken to ensure that the neutral conductor of the threephase voltage transformer does not remain connected with the neutral of the three-phase power supply, as other wise a short-circuit to ground would occur, which would cause an overload.

Set again the supply voltage to UL12 = 380 V and measure the voltage at the terminals “n” and “e” of the three individual auxiliary windings connected in series:

Uen = ……… V

and interpret this measurement result with the help of the following phasor diagram.

EXPERIMENT NO. 11

TWO SINGLE-POLE VOLTAGE TRANSFORMERS

Objectives:

- Assembling a voltage transformer circuit in open delta connection.

- Measuring the three conductor voltages on symmetrical and asymmetrical loads.

Equipments:

- 1 IT 6000 Three-phase power supply

- 1 IT 6046 Three-phase voltage transformer

- 4 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

EXPERIMENT N°8: TWO SINGLE-POLE VOLTAGE TRANSFORMERS

Experiment procedure

Assemble the circuit according with the foregoing topographic diagram.

Do not forget that the voltage transformer must never be short-circuited on the secondary side!

The three-phase voltage transformer is connected as two single-pole isolated transformers in open delta connection and provides an image of the three conductor voltages: this circuit can be used for measurement only in the case of symmetrical operation.

Set the supply voltage to UL12 = 380 V and measure the three conductor voltages on the secondary side:

U1 = Uwu ……… V

U2 = Uue ….…… V

U3 = Uwe ……… V

and interpret these measurement results with the help of the following phasor diagram.

In the symmetrical load operation the open delta configuration responds according to the transformation ratio.

Now set up the asymmetrical operating state by breaking one phase at a time between the three-phase power supply and the voltage transformer.

Repeat the above measurements and enter the measured values in the following table.

| Disconnected phase | U1 (V) | U2 (V) | U3 (V) |
| --- | --- | --- | --- |
| L1 L2 L3 | ……… (100) ………. (100) ………. (100) | ……… (0) ………. (50) ………. (100) | ……… (100) ………. (50) ………. (0) |

Note: The values in brackets are for information only.

In the asymmetrical load operation the open delta configuration reacts with partially false measurement results and it cannot be used for measurement on asymmetrically operated networks.

EXPERIMENT NO. 12

SERIES CONNECTION OF TWO LINES

Objectives:

- Measurement of the voltage distribution in the series connection of two lines.

- Investigation of the effect of the operating capacitances on the voltages and currents.

Equipments:

- 2 IT 6002 Overhead line model

- 1 IT 6000 Three-phase power supply

- 1 IT 6004 Resistive load

- 1 IT 6003 Three-phase transformer

- 1 IT 6019 Power circuit breaker

- 3 IT 6035 Moving iron ammeter (2.5 A)

- 3 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

EXPERIMENT N°1.1: TWO LINES IN SERIES

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Set primary-side of the three-phase transformer in delta connection 380V and using bridging plugs set the secondary-side to star UN + 5%.

Remove all bridging plugs connecting the capacitances to both line models.

Connect a three-phase balanced resistive load to end terminals of the line 2; set the load resistance value to R1.

Adjust the supply voltage in order to obtain the nominal voltage UN = 380V (phase-to-neutral voltage 220V) at the beginning of line 1: this value must kept constant for all the measurements.

Beginning from the R1 value reduce the resistive load in steps till the R6 value. For each step measure the following quantities:

voltage UB at the beginning of line 2 and voltage UE at load and the load current IE, also current through the two lines.

Enter the measured value into the following table

| UA (V) | R | UB (V) | UE (V) | IE (A) |
| --- | --- | --- | --- | --- |
| 220 | R1 |  |  |  |
| 220 | R2 |  |  |  |
| 220 | R3 |  |  |  |
| 220 | R4 |  |  |  |
| 220 | R6 |  |  |  |
| 220 | R7 |  |  |  |

Plot the voltage curves as a function of the load current in a combined diagram

The voltages decrease from the infeed point to the end of the lines series.

Typical results

The voltage values at the load show that the voltage drops are impermissibly large with very long line

EXPERIMENT N°1.2: TWO LINES IN SERIES

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

Set primary-side of the three-phase transformer in delta connection 380V and using bridging plugs set the secondary-side to star UN + 5%.

Remove all bridging plugs connecting the capacitances to both line models.

Connect a three-phase balanced resistive load to end terminals of the line 2; set the load resistance value to R1.

Adjust the supply voltage in order to obtain the nominal voltage UN = 380V (phase-to-neutral voltage 220V) at the beginning of line 1: this value must kept constant for all the measurements.

Beginning from the R1 value reduce the resistive load in steps till the R5 value. For each step measure the following quantities:

current I1 at the beginning line 1, voltage UB and current I2 at the beginning line 2, voltage UE and current IE at the load.

Enter the measured value into the following table

| UA (V) | R | I1 (A) | UB (V) | I2 (A) | UE (V) | IE (A) |
| --- | --- | --- | --- | --- | --- | --- |
| 220 | R1 |  |  |  |  |  |
| 220 | R2 |  |  |  |  |  |
| 220 | R3 |  |  |  |  |  |
| 220 | R4 |  |  |  |  |  |
| 220 | R5 |  |  |  |  |  |

Plot the voltage and the line currents curves as a function of the load current in a combined diagram

.

Typical results

When the line capacitances are taken into consideration cross currents flow at beginning and end points of the two line models. These cross currents are superposed on the load current. Moreover the influence of the line inductances on the voltage drop is partially compensated by the effect of the cross capacitances.

EXPERIMENT No. 13

PARALLEL CONNECTION OF TWO LINES

Objectives:

- Measurement of the current distribution in the parallel connection of two lines.

- Investigation of the effect of the operating capacitances on the voltages and currents

Equipments:

- 2 IT 6002 Overhead line model

- 1 IT 6000 Three-phase power supply

- 1 IT 6004 Resistive load

- 1 IT 6005 Inductive load

- 1 IT 6003 Three-phase transformer

- 1 IT 6019 Power circuit breaker

- 3 IT 6035 Moving iron ammeter (2.5 A)

- 3 IT 6038 Moving-iron voltmeter (125 - 250 - 500 V)

EXPERIMENT N°2.1: TWO LINES IN PARALLEL

Experiment procedure

Assemble the circuit according with the foregoing topographic diagram.

Set primary-side of the three-phase transformer in delta connection 380V and using bridging plugs set the secondary-side to star UN + 5%.

Remove all bridging plugs connecting the capacitances to both line models.

Connect a three-phase balanced ohmic-inductive load to end terminals of the

parallel-connected lines: set the load value to R1 – L1.

Adjust the supply voltage in order to obtain the nominal voltage UN = 380V (phase-to-neutral voltage 220V) at the beginning of the parallel-connected lines: this value must be kept constant for all the measurements.

Beginning from R1 – L1 value change the load in steps for the indicated values.

For each step measure the following quantities: current I1 at the beginning of line 1, current I2 at the beginning of line 2, current IE and voltage UE through the load.

Enter the measured value into the following table.

| UA (V) | R – L | I1 (A) | I2 (A) | IE (A) | UE (V) |
| --- | --- | --- | --- | --- | --- |
| 220 | R1 - L1 |  |  |  |  |
| 220 | R2 - L2 |  |  |  |  |
| 220 | R3 – L3 |  |  |  |  |
| 220 | R4 – L4 |  |  |  |  |
| 220 | R5 – L5 |  |  |  |  |

Temporarily disconnect one of the lines and repeat the above measurements.

| UA (V) | R – L | I1 (A) | I2 (A) | IE (A) | UE (V) |
| --- | --- | --- | --- | --- | --- |
| 220 | R1 - L1 |  | 0 |  |  |
| 220 | R2 - L2 |  | 0 |  |  |
| 220 | R3 – L3 |  | 0 |  |  |
| 220 | R4 – L4 |  | 0 |  |  |
| 220 | R5 – L5 |  | 0 |  |  |

Plot the load as a function of the load current for the two working conditions in a combined diagram.

Typical results

As expected, when two equally long lines are connected in parallel, each lines carries half the load current If one of the lines is disconnected, the remaining line now carries twice as much current, causing an higher voltage drop.

EXPERIMENT N°2.2: TWO LINES IN PARALLEL

Experiment procedure

Assemble the circuit according with the foregoing topographic diagram.

Set the primary-side of the three-phase transformer in delta connection 380V and using bridging plugs set the secondary-side to star UN + 5%.

Insert all bridging plugs connecting the capacitances to both line models.

Connect a three-phase balanced ohmic-inductive load to end terminals of the

parallel-connected lines: set the load value to R1 – L1.

Adjust the supply voltage in order to obtain the nominal voltage UN = 380V (phase-to-neutral voltage 220V) at the beginning of the parallel-connected lines: this value must kept constant for all the measurements.

Beginning from R1 – L1 value change the load in steps for the indicated values.

For each step measure the following quantities: current I1 at the beginning of line 1, current h at the beginning of line 2, current IE and voltage UE through the load.

Enter the measured value into the following table.

| UA (V) | R – L | I1 (A) | I2 (A) | IE (A) | UE (V) |
| --- | --- | --- | --- | --- | --- |
| 220 | R1 - L1 |  |  |  |  |
| 220 | R2 - L2 |  |  |  |  |
| 220 | R3 – L3 |  |  |  |  |
| 220 | R4 – L4 |  |  |  |  |
| 220 | R5 – L5 |  |  |  |  |

Plot the load voltage and the current at the current at the beginning lines as a function of the load current in a combined diagram.

.

Typical results

As expected, consideration of operating capacitances result in better voltage values.

EXPERIMENT NO. 14

ISOLATED NEUTRAL POINT SYSTEM: FAULT-TO-EARTH

Objectives:

- Investigating the performance of a transmission line with isolated neutral point connection in the case of a fault to earth.

- Carrying out measurements of the earth-fault current and the voltage rise of the healty phases.

Equipments:

- 1 IT 6017 Three-phase power supply unit

- 1 IT 6019 Power circuit breaker

- 1 IT 6003 Three-phase transformer

- 1 IT 6002 Overhead line model

- 1 IT 6035 Moving-iron ammeter (2,5 A)

- 1 IT 6037 Moving-iron voltmeter (600 V)

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram. Set the primary side of three-phase transformer in delta connection 380 V and using bridging plugs set the secondary-side to star UN – 15%.

DO NOT CONNECT the neutral star point to neutral N conductor.

Insert all bridging plugs connecting the capacitances to overhead line model. Set the supply voltage to UN = 380 V.

Measure the earth-fault current Ie as well as the voltages on both healthy phases L2 and L3 with respect to earth :

IE = …………… (A) 	U2 = …………… (V) 	U3 = …………… (V)

Compare the earth-fault current measured to the value which would be expected according to the theory:

where U is the voltage present at the fault location during normal operation.

EXPERIMENT NO. 15

PETERSEN SUPPRESSION COIL

Objectives:

- Determining the inductance of an earth-fault neutralizer for the overhead line model.

- Investigating the performance of a transmission line with a fault and comparing the current value with those determined during earth-fault with isolated neutral point system in experiment 6.

Equipments:

- 1 IT 6017 Three-phase power supply unit

- 1 IT 6019 Power circuit breaker

- 1 IT 6003 Three-phase transformer

- 1 IT 6023 Petersen coil

- 1 IT 6002 Overhead line model

- 1 IT 6035 Moving-iron ammeter (2,5 A)

- 1 IT 6037 Moving-iron voltmeter (600 V)

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram. Set primary-side of three-phase transformer in delta connection 380 V and using bridging plugs set the secondary-side to star UN - 15%.

CONNECT THE NEUTRAL STAR POINT TO NEUTRAL N CONDUCTOR VIA THE PETERSEN COLL.

Insert all bridging plugs connecting the capacitance to overhead line model.

Set the supply voltage to UN = 380 V.

In order to determine the required inductance for the compensation coil, the earth-fault residual current as a function of the inductance used has to be measured for the following values listed in the table (To achieve more precise measurement results it is recommended that you use a sensitive ammeter with mA-measurement range).

| L (mH) | 2000 | 1800 | 1600 | 1400 | 1250 | 1100 | 740 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IE (A) |  |  |  |  |  |  |  |

Sketch the curve of the earth-fault residual current as a function of the compensation coil inductance used:

The minimum earth-fault residual current is achieved at a Petersen coil inductance

Lp = ………… mH.

At the frequency of 50 Hz the theoretical value of this inductance is

Measure the voltages of the two healthy phases with respect to earth at the fault location while using the compensation coil which is tuned to the overhead line model:

U2 = ………… (V) 		U3 = ………… (V)

and verify that these voltages are smaller than in the case of the earth fault with isolated neutral point system.

EXPERIMENT NO. 16

PARALLEL COMPENSATION

Objectives:

- Investigating the effect of parallel compensation on the voltage stability at the load and the transmission losses of the line.

Equipments:

- 1 IT 6017 Three-phase power supply unit

- 1 IT 6019 Power circuit breaker

- 1 IT 6003 Three-phase transformer

- 1 IT 6002 Overhead line model

- 1 IT 6004 Resistive load

- 1 IT 6005 Inductive load

- 1 IT 6006 Capacitive load

- 1 IT 6048 Power meter

- 1 IT 6049 Power factor meter

- 2 IT 6035 Moving-iron ammeter (2,5 A)

- 2 IT 6037 Moving-iron voltmeter (600 V)

Experiment procedure

Assemble the circuit in accordance with the foregoing topographic diagram.

The inductive component of an ohmic-inductive load is to be compensated using a

capacitance connected in parallel.

In order to demonstrate the significant features of the parallel compensation, it is sufficient to investigate the line without capacitances. This also ensures conformity with the equivalent circuit diagram and corresponding vector diagram presented in the theoretical section (point 1.7.1, Fig.17).

Remove all bridging plugs connecting capacitances CE and CL on the overhead line model. Set primary-side of three-phase transformer in delta connection 380 V and using bridging plugs set the secondary-side to star UN + 5%.

Set the supply voltage to UN = 380 V.

Set the value L2 = 3.19 H at the inductive load: a capacitance of exactly 3.2 μF would be required to compensate for this inductance completely (ω • C • L = 1).

Connect the value C2 = 3 μF at the capacitive load and measure the voltage U1, the current I1, the active P1 and reactive Q1 powers at the beginning of the line and the voltage U2, the current I2 and cosφ2 at the line end for various settings of the load resistance. Enter the measured values in the following table.

Inductive load L2 = 3.19 H Compensation capacitance C2 = 3 μF

| R | U1 (V) | I1 (A) | P1 (W) | Q1 (Var) | U2 (V) | I2 (A) | cosφ2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  |  |  |  |  |  |
| R2 |  |  |  |  |  |  |  |
| R3 |  |  |  |  |  |  |  |
| R4 |  |  |  |  |  |  |  |

Repeat the above measurements for different inductive loads and compensation capacitances.

Inductive load L4 = 1.27 H Compensation capacitance C4 = 8 μF

| R | U1 (V) | I1 (A) | P1 (W) | Q1 (Var) | U2 (V) | I2 (A) | cosφ2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  |  |  |  |  |  |
| R2 |  |  |  |  |  |  |  |
| R3 |  |  |  |  |  |  |  |
| R4 |  |  |  |  |  |  |  |

Inductive load L5 = 0.9 H Compensation capacitance C5 = 10 μF

| R | U1 (V) | I1 (A) | P1 (W) | Q1 (Var) | U2 (V) | I2 (A) | cosφ2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  |  |  |  |  |  |
| R2 |  |  |  |  |  |  |  |
| R3 |  |  |  |  |  |  |  |
| R4 |  |  |  |  |  |  |  |

Comparing the measurement results with those obtained under experiment 4, parallel compensation reduces the reactive power requirement of the line-load system; at the same time, the voltage at the load increases .

The compensation is virtually total and this may be seen from load cosφ2 which is now approx 1 in every case.

In the following experiment the power factor of a load is to improved through compensation to a specific value.

From measurement results of experiment 4 (ohmic-inductive load) with inductive load L5 = 0.9 H and resistive load R3 = 435 Ω we know that a cosφ2 value of about 0.5 occurs for this load case.

Set the inductive load Ls and resistive load R3.

In order to determine the required capacitance for improving the power factor to about 0.9 change in steps the capacitance load values until power factor meter reads about 0.9. At this moment measure voltage U1, current I1, active Pi and reactive Q1 powers at the beginning of the line and voltage U2, current I2 and cosφ2 at the line end.

Compensation capacitance: ………… μF

U1 = …………… V 	I1 = …………… A 		P1 = …………… W

Q1 = …………… Var 	U2 = …………… V 	I2 = …………… A

cosφ2 = ……………

Comparing these measurement results with those obtained under same ohmic-inductive load in the experiment 4, here, too, we see a significant improvement in the voltage at consumer, coupled with a reduction current. Moreover the desired power factor value can be achieved precisely.